EXPERT REPORT ON THE SIZES AND TECHNOLOGIES OF MECHANICAL JOINTING OF CONSTRUCTION REINFORCEMENT IN GLOBAL NUCLEAR PROJECTS OF THE GEN III+ GENERATION

I. INTRODUCTION AND THE REGULATORY IMPERATIVE OF NUCLEAR REINFORCEMENT 	2

1.1 Fundamental Role of Valves in Critical Structures of Nuclear Power Plants 	2

1.2. Basic Standards and Requirements for Connections 	2

1.3. Bar Break Principle and Yield Strength Requirements 	3

II. TYPOLOGY OF REINFORCING BARS AND THE PROBLEM OF MASSIVENESS 	4

2.1. Diameter Ranges in Nuclear Construction 	4

2.2. Cross-Analysis of Metric and Imperial Sizes 	4

2.3. The Impact of Large Diameter on Splicing Technologies 	5

III. CLASSIFICATION AND TECHNOLOGIES OF MECHANICAL COUPLINGS 	6

3.1. Main Categories of Mechanical Couplings Used in Nuclear Power Plants 	6

3.2 Key Benefits of Mechanical Splicing in the Nuclear Sector 	8

IV. GLOBAL CROSS-ANALYSIS OF SPLICING TECHNOLOGIES ACCORDING TO PROJECTS 	9

4.1. FRANCE (EPR) 	9

4.2. AMERICA (AP1000) 	9

4.3. KOREA (APR-1400) 	10

4.4. RUSSIA (VVER-1200) 	10

4.5. CHINA (HPR1000/Hualong One) 	10

V. KEY MANUFACTURERS OF COUPLINGS AND THEIR CERTIFICATION 	11

5.1. Dextra Group: Leadership in Extrusion Systems (Griptec®) 	11

5.2. nVent LENTON (ERICO): US Dominance and Taper Thread Tradition 	12

VI. SUMMARY ANALYSIS AND ENGINEERING RECOMMENDATIONS 	13

6.1. Comparative Table of Application of Splicing Technologies 	13

6.2. Performance Evaluation of Couplings 	15

6.3. Engineering Recommendations 	15

VII. CONCLUSION: STRATEGIC IMPLICATIONS 	16

I. INTRODUCTION AND THE REGULATORY IMPERATIVE OF NUCLEAR REINFORCEMENT

1.1 The Fundamental Role of Valves in Critical Nuclear Power Plant Structures

Reinforcement is a critical component for the structural integrity and safety of third-generation (Gen III+) nuclear power plants (NPPs). The highest demands are placed on the reinforcement of the reactor containment vessel (NPP) and the basemat (NPP basemat). 1 The containment of modern reactors, such as the APR1400 or EPR, is a prestressed concrete structure with a steel lining, designed to withstand extreme loads. 1

These extreme loads include internal pressure in the event of a failure, thermal stresses, and external influences such as seismic activity, falling heavy objects (such as aircraft), and shock waves. To effectively resist these forces, reinforcement must provide not only high tensile and compressive strength but also guaranteed ductility and energy dissipation capacity under cyclic and seismic loads. 3

For example, in the APR1400 reactor design (Korea/USA), the containment vessel is a cylinder with a hemispherical dome, resting on a common foundation slab, with a constant cylindrical thickness of 1.37 meters (4 feet 6 inches). 1 The massiveness of these structures and the need to accommodate a huge number of reinforcing bars while maintaining the quality of the concrete determine the need for advanced joining technologies.

1.2 Basic Standards and Requirements for Connections

The design and construction of critical nuclear structures is governed by the strictest international and national standards.

- American Standard (De Facto International Benchmark): The key document is the ASME Boiler and Pressure Vessel Code, Section III, Division 2 (ACI 359/CC-3500) , which regulates the design of concrete containment shells. This standard establishes safety categories for materials and defines the types of connections permitted for use in these structures.

- European Standard: European projects such as EPR use Eurocode 2 for concrete design and Eurocode 8 (EN 1998-1) for seismic performance. Eurocode 8 specifically requires that steel used in critical regions of primary seismic elements have high uniform plastic elongation. 3

- Russian standard: Rosatom projects (VVER-1200) use Russian regulatory documents, such as GOST and PNAE G regulations. However, when implementing export projects (for example, in Turkey), confirmation of compliance with international quality and safety standards is often required.

1.3. Bar Break Principle and Yield Strength Requirements

In nuclear engineering, a key engineering principle applicable to all splicing technologies is the requirement for "Full Performance" or "Bar Break System" . 3

The "Bar Fracture" principle states that the strength of a reinforcement connection should be such that, during a tensile test, failure occurs in the intact reinforcement bar, not in the connection area itself (the coupling). 3 This ensures that the connection does not become the weakest link in the structure.

The regulatory requirements for these connections are extremely stringent. For example, recent changes to the ASME BPV Code require that mechanical splices exhibit a minimum tensile strength greater than 1.25 times the actual yield strength (YS) of the reinforcing bar. 6 This requirement is significantly more stringent than using the nominal yield strength and is intended to ensure that under extreme loads (especially seismic), the structure exhibits the desired ductile behavior, in which failure is predictable and occurs in the bar rather than in a brittle joint. 6

The high regulatory stringency in the nuclear sector, requiring maximum strength and guaranteed traceability, leads to a high degree of technology standardization. This means that, regardless of the country of origin (Russia, Korea, the United States, or France), leading global suppliers of mechanical systems for critical structures strive for a unified certification system. Market analysis shows that companies such as Dextra and nVent LENTON certify their products to ASME NCA-3800 and ISO 19443 (the quality management system standard for organizations in the nuclear supply chain). This indicates that ASME BPV Code Section III, Division 2, effectively serves as a global compliance standard for Safety Class 1 building materials, transcending geographic and vendor boundaries.

II. TYPOLOGY OF REINFORCING BARS AND THE PROBLEM OF MASSIVENESS

2.1. Diameter Ranges in Nuclear Construction

Large-diameter reinforcement bars (D > 25 mm) predominate in Gen III+ NPP structures, particularly in the containment vessel, foundation slab, and reactor building walls. 8 The use of such massive bars is required to absorb the enormous forces generated in these thick-walled structures. 1

Typical diameters used in main nuclear load-bearing structures include:

- 25–36 mm (metric, Ø25–Ø36): Used for reinforcing the walls of auxiliary buildings and for medium reinforcement of containment.

- 40–57 mm (metric, Ø40–Ø57): These are critical dimensions for foundation slabs, ring reinforcement, and areas of maximum load and anchorage where maximum resistance is required. In the American system, this corresponds to sizes #14 and #18 .

2.2. Cross-Analysis of Metric and Imperial Sizes

In the global nuclear power industry, two main valve designation systems coexist, complicating logistics and design. Designs developed in the United States (AP1000) or with American engineering heritage (APR-1400, partially based on System 80+) use the imperial system (ASTM/ACI), where the size is designated by a number corresponding to eighths of an inch. European, Russian, and Chinese designs predominantly use the metric system (mm).

The following table provides a comparison of critical nuclear construction sizes:

Table 2.1: Comparison of Critical Reinforcement Sizes in Nuclear Construction

| Designation (USA, ASTM) | Nominal Diameter (inches) | Nominal Diameter (mm) | Approximate Metric Designation (Europe/Russia) | Typical Application in Nuclear Power Plants |
| --- | --- | --- | --- | --- |
| #8 | 1,000 | 25,400 | Ø25 | Walls of auxiliary buildings |
| #10 | 1.270 | 32.260 | Ø32 | Medium containment reinforcement |
| #11 | 1.410 | 35,810 | Ø36 | Foundation slabs, ring reinforcement |
| #14 | 1.693 | 43,000 | Ø40 / Ø45 | Massive structures (base plate) |
| #18 | 2.257 | 57,300 | Ø50 / Ø57 | Maximum load and anchorage zones |

2.3. The Impact of Large Diameter on Splicing Technologies

The increase in rebar diameter typical for Gen III+ NPPs has dramatically increased the limitations of the traditional lap splice technology .

Limitations of Lap Splicing

- Strength and Length Loss: The lap must be long enough to provide adequate bond strength to allow force transfer between the bars before they reach yield strength. 9 For larger diameters, an exponential increase in lap length is required. Building codes (e.g., UBC) recommend avoiding laps for rebar larger than #11 (Ø36 mm) in critical areas. 10

- Rebar Congestion: The most serious problem. Lap splicing requires doubling the number of rebars in the splice area. In the massive, densely reinforced structures of the nuclear island, this creates critical congestion. 3 Such congestion physically restricts the flow of concrete mix and aggregates (crushed rock), preventing proper consolidation of the concrete. Insufficient consolidation leads to the formation of voids (voids), which critically reduces the density and, consequently, the protective and load-bearing properties of the concrete shell, which is unacceptable in nuclear structures. 11

Therefore, the choice of connection technology in Gen III+ projects is not simply a matter of cost effectiveness, but a technological imperative to ensure the quality of concreting. The continued increase in structural mass and the tightening of seismic requirements in Gen III+ projects (such as the APR1400 with a wall thickness of 1.37 m² ) necessitated the transition to mechanical couplings.

A technological necessity . Mechanical splicing eliminates the need for doubling reinforcement in the connection area, reducing clutter and improving the homogeneity of the concrete, thereby ensuring the achievement of the designed reinforcement density and the quality of protective structures.

III. CLASSIFICATION AND TECHNOLOGIES OF MECHANICAL COUPLINGS

In nuclear construction, mechanical splices have become the preferred method because they ensure load path continuity with predictable strength equivalent to that of the rod itself. 11 Traditional methods, such as welded joints, are of limited use because they can alter the metallurgical properties of the steel and require complex, weather-sensitive quality control.

3.1. Main Categories of Mechanical Couplings Used in Nuclear Power Plants

Mechanical couplings qualified for use in nuclear structures (according to, for example, ASME CC-3500) are divided into the following main categories:

3.1.1. Threaded Systems

This type requires preliminary preparation of the ends of the reinforcing bar using specialized equipment.

- Tapered Thread: In this method, tapered threads are cut into the ends of the reinforcing bar and the connection is made using a standard coupling. 12 For assembly, one of the bars must be able to rotate. Examples: 
nVent LENTON (LENTON®) systems . These are widely used in the USA (AP1000) for columns and other elements where bar rotation is possible. 13

- Upset Parallel Threaded (Bartec/Fortec): To meet the "Bar Break" requirement, the end of the rebar is cold-swaged (or expanded) before the parallel threads are cut, artificially increasing its diameter. This compensates for the loss of cross-sectional area caused by the threading, ensuring that the joint strength exceeds the strength of the rebar itself. 4 Examples: Dextra Bartec® / Fortec® systems 
. These are designed for rebar diameters from 12 to 50 mm. 4

3.1.2. Swaged / Extruded Systems

These systems provide a connection through plastic deformation of the metal of the coupling and the rod, often without the need for rotation of the rods.

- Extruded Systems (Griptec®): The rebar is inserted into a sleeve, and the sleeve is then subjected to a high-strength, monolithic extrusion using powerful hydraulic equipment. This creates a high-strength, monolithic connection that is ideal for positional (non-retractable) joints. 15 The Dextra Griptec® system 
often uses a male/female sleeve configuration to ensure positional assembly and is preferred by the nuclear industry. 4

- Crimping Systems: The connection is achieved by pressing the crimping sleeve around the rod using hydraulic equipment. Example: Bartek BP. 17

3.1.3. Systems for Positional Splicing and Anchoring

For complex assemblies where the rods are already fixed (for example, when connecting precast concrete panels or for closing openings), special positional couplers are used (nVent LENTON Position Couplers, Griptec Bridging Assemblies). 15 Also widely used

Headed Bars/Terminators are attached to the end of a rebar, replacing the traditional hook and providing anchorage in confined spaces, further reducing rebar clutter. 16

3.2. Key Benefits of Mechanical Splicing in the Nuclear Sector

The advantages of mechanical couplings provide a critical contribution to the safety and quality of Gen III+ NPP construction:

- Guaranteed Strength and Ductility: "Full Performance" couplings ensure that the connection strength meets or exceeds the bar break strength, ensuring the required ductile behavior of the structure under seismic and cyclic loading. 3

- Reduced Clutter: Eliminating overlaps allows for a significant reduction in the amount of reinforcement, facilitating the flow and consolidation of concrete in thick-walled elements. 11

- Improved Cycle Performance: Unlike lap joints, which have poor cyclic performance and require additional reinforcement for confinement 11 , mechanical couplings exhibit performance similar to continuous bar.

- Quality Assurance (QA/QC): Ability to control the quality of every connection. The most advanced systems, such as Dextra Griptec®, include 100% automated testing of every connection during installation, providing an unprecedented level of traceability and quality assurance (QA/QC). 15

The requirement for maximum strength combined with guaranteed traceability is a decisive selection factor in the nuclear industry. Systems offering automated quality control and traceability of each component 7 have a clear advantage in projects with the highest safety requirements (Safety-Class 1). This justifies Griptec's positioning as the "preferred system for nuclear reactor buildings worldwide." 4 The choice of coupling is thus determined not only by its technical strength but also by the system's ability to ensure traceability and non-destructive testing, a vital management and engineering decision.

IV. GLOBAL CROSS-ANALYSIS OF SPLICING TECHNOLOGIES BY PROJECT

The analysis examined key Gen III+ projects in Russia, Korea, the United States, China, and France. Despite differences in reactor design (PWR, EPR, VVER), a general trend toward the use of the same internationally certified mechanical splicing systems is evident.

4.1. FRANCE (EPR)

- Projects: Flamanville 3 (France) and Hinkley Point C (UK). 20

- Reactor Technology: European Pressurized Water Reactor (EPR), Gen III+, developed by Framatome and EDF. The design includes a prestressed concrete containment vessel.

- Splicing Technology: The primary splicing method, especially at critical joints and when assembling large reinforced concrete panels, is cold extrusion.

- Manufacturer and Type: Dextra Group supplies its Griptec® system . 4 On the Flamanville 3 project, construction of which began in 2008, more than 800,000 Griptec® connections were used. 15 Around 400,000 of these were positional assemblies, highlighting Griptec®'s applicability for connecting large-diameter rebar without the need for rotation—a key advantage in densely reinforced structures.

- Additional Solutions: Griptec® is used at Hinkley Point C (also EPR), as are Bartec® and Pressed Connection (PC) Headed Bars. 22

4.2. AMERICA (AP1000)

- Projects: Vogtle Units 3 & 4 (USA). 23

- Reactor Technology: AP1000, Westinghouse Gen III+ pressurized water reactor, known for its simplified and passive safety systems. 25

- Standard: Construction is carried out in accordance with the highest requirements of ASME BPV Section III, Division 2 (CC-3500) and ACI 349, using the ASTM imperial rebar size system (#).

- Splicing Technology: Mechanical threaded systems are used, as well as exothermic (welded) connections for the most critical areas.

- Manufacturer and Type: nVent LENTON (formerly ERICO) is a leading supplier of rebar splicing, anchoring, and connection systems in the United States . The company supplies:

  - LENTON® (tapered thread system) for standard connections where rod rotation is possible. 12

  - CADWELD® Rebar Splices are a highly reliable mechanical system that has traditionally been recommended for extremely high safety requirements such as nuclear containment structures, providing strength similar to intact bar. 5

4.3. KOREA (APR-1400)

- Projects: Barakah Nuclear Energy Plant (UAE) 26 , Shin-Kori (South Korea).

- Reactor Technology: KEPCO's Advanced Power Reactor 1400 (APR-1400), Gen III+, which has received US NRC certification and European Utility Requirements (EUR) approval. 26

- Splicing Technology: Because APR-1400 is an evolution of the American System 80+ design and is NRC certified, the use of Type 2 (Bar Break) mechanical splices complying with ASME CC-3500 is mandatory. 6

- Manufacturer and Type: Although the specific coupling manufacturer for the Barakah project is not publicly identified, compliance with strict NRC and EUR standards means that only systems from globally certified suppliers, such as Dextra (Griptec®/Bartec®) or nVent LENTON (LENTON®/CADWELD®), can be used. These systems must be capable of handling the large diameters typical of this reactor type.

4.4. RUSSIA (VVER-1200)

- Projects: Akkuyu Nuclear Power Plant (Turkey). 29

- Reactor Technology: The VVER-1200 pressurized water reactor, developed by Rosatom, belongs to the Gen III+ generation.

- Splicing Technology: Historically, welding or lap splicing has been the predominant method in Russian practice, but modern export projects are transitioning to advanced mechanical couplings to meet international safety standards and speed up construction.

- Manufacturer and Type: Analysis shows that Dextra Group confirms the delivery of its Bartec® and Griptec® systems for the Akkuyu Nuclear Power Plant (NPP) in Turkey. 16 This provides direct evidence that the same "Rod Break" systems are used for critical structures (such as the containment) in Russian export projects as in European (EPR) projects.

4.5. CHINA (HPR1000/Hualong One)

- Projects: Fuqing 5/6 (China). 32

- Reactor Technology: HPR1000 (Hualong One), developed by China National Nuclear Corporation (CNNC), is a Chinese Gen III+ reactor with double containment and a combination of active and passive safety systems. 32

- Splicing Technology: Strict ductility and seismic resistance requirements similar to European standards require the use of full performance systems.

- Manufacturer and Type: International suppliers such as Dextra Group are actively involved in Chinese projects, offering Bartec® and Griptec® solutions to ensure high performance and quality connections. 14

A cross-analysis reveals a high degree of homogenization of mechanical rebar splicing technologies. Regardless of the reactor developer (Rosatom, KEPCO, Framatome, Westinghouse), all global Gen III+ projects select a limited set of systems capable of meeting the highest strength, ductility, and traceability requirements, dictated primarily by ASME and Eurocode 8 standards. This strategic decision is aimed at reducing regulatory and construction risks.

V. KEY MANUFACTURERS OF COUPLINGS AND THEIR CERTIFICATION

The global market for nuclear-qualified mechanical couplings is dominated by two major international companies: Dextra Group (headquartered in France/Thailand) and nVent LENTON (USA, formerly ERICO). Their success in this industry is due to their ability to undergo rigorous multi-stage certification.

5.1. Dextra Group: Leadership in Extrusion Systems (Griptec®)

Founded by French entrepreneurs in 1983, Dextra Group is a global leader in the production of engineered building products. 34

Griptec® System

Griptec® is a cold extrusion rebar splicing system marketed as an advanced full-performance system (tension/compression/cyclic loading/fatigue) .

- Technical Advantage: The Griptec® system is ideal for use in nuclear reactor buildings because it allows for high-strength connections without rod rotation. 15

- Application: Widely used in French (Flamanville 3) 15 and Russian export (Akkuyu VVER-1200) 16 projects.

- Quality Control and Certification: Griptec®'s key competitive advantage is its unique quality assurance process: 100% of manufactured connections undergo automated testing as part of a standard cycle. 15 Griptec® coupling and anchor plate production is certified to the highest standards, including 
ISO 9001, ISO 19443:2018 (Nuclear QMS), and ASME NCA-3800 quality assurance standards , which meets the requirements of ASME NQA-1 and 10CFR50 Appendix B. 7 This confirms that the company complies with the US Federal Regulations for Suppliers of Class 1 Safety Equipment for Nuclear Power Plants.

Bartec® / Fortec® System

Bartec® is a parallel thread system with an increased shank end diameter that also provides "Shield Break" strength. 14 It complies with ACI 318, IBC, AASHTO, Eurocode 2 and ASME Sec III Div 2 . 4 The use of Bartec® has also been confirmed at the Akkuyu NPP (VVER-1200). 16

5.2. nVent LENTON (ERICO): US Dominance and Taper Thread Tradition

nVent LENTON is a global leader in mechanical rebar splicing systems, with a long history of innovation in this field. 13

LENTON® Systems

Launched in 1974, the LENTON® Taper Threaded Rebar Splice system is one of the most widely used tapered thread systems in the world. 18

- Product Line: Includes standard couplers (for rotating bars) 12 , positional couplers (for non-rotating or pre-bent bars) 18 , and LENTON® TERMINATOR end anchors, which are used to reduce rebar clutter by replacing hooks. 19

- Strategic Applications: LENTON® systems are used in nuclear power plant structures (including the AP1000 in the US) and other critical infrastructure (railways, subways). 11

CADWELD®

CADWELD® is a mechanical system that has historically proven itself in the most demanding applications. 19 It is based on an exothermic process or mechanical crimping. CADWELD® is recommended for structures with extremely high safety requirements, such as nuclear containment vessels, as it provides high tensile strength. 5

Both Dextra and nVent LENTON possess a de facto "nuclear passport" thanks to dual certification (ASME/ISO 19443). This global standardization of critical components is key to enabling reactor developers (such as Rosatom, KEPCO, and Framatome) to utilize proven and qualified solutions anywhere in the world, reducing project logistical and regulatory risks.

VI. SUMMARY ANALYSIS AND ENGINEERING RECOMMENDATIONS

6.1. Comparative Table of Application of Splicing Technologies

The following table summarizes the key characteristics of the reinforcement and splicing technologies used in the world's leading Gen III+ NPP projects.

Table 6.1: Summary Analysis of Rebar Splicing Technologies in Gen III+ Nuclear Power Plant Projects

| Country/Technology | Example Project | Critical Diameter (mm) | Connection Standard | Basic Coupling Type | Key Manufacturer | Confirmation of Application |
| --- | --- | --- | --- | --- | --- | --- |
| France (EPR) | Flamanville 3, Hinkley Point C |  | Eurocode 8, RCC-M, ASME Type 2 | Extruded (Griptec®) | Dextra Group | Over 800,000 connections on Flamanville 3, 100% QA/QC 4 |
| USA (AP1000) | Vogtle 3 & 4 | #14 – #18 ( ) | ASME CC-3500 Type 2, ACI 349 | Tapered thread (LENTON®) / CADWELD | nVent LENTON (ERICO) | A key supplier of systems for US nuclear designs 18 |
| Korea (APR-1400) | Barakah (UAE) |  | ASME CC-3500 Type 2, US NRC, EUR | Full Performance (Tapered/Swaged) | nVent LENTON / Dextra (certified) | Compliance with NRC/EUR standards 26 required |
| Russia (VVER-1200) | Akkuyu (Türkiye) |  | GOST, international QA/QC | Parallel/Extruded (Bartec®, Griptec®) | Dextra Group | Confirmed use of Dextra at site 16 |
| China (HPR1000) | Fuqing 5/6 |  | Chinese standards (Gen III+) | Full Performance (Localized/Dextra) | Dextra Group / Local Producers | Requirement for high ductility and seismic resistance 14 |

6.2. Performance Evaluation of Couplings

The choice between leading splicing systems is determined by the specifics of the construction process and the criticality of the structure:

- Griptec (Extrusion): The main advantage is the highest level of quality control (100% automated testing) and the suitability for positional splicing, which is indispensable in modular construction (e.g., precast concrete panel assembly) and densely reinforced assemblies. 7 Disadvantage: the system requires powerful and bulky hydraulic equipment on site.

- LENTON/Bartec (Threaded Systems): Advantages include relative ease of rod preparation (although Bartec requires a larger diameter) and high installation speed, provided the rod can rotate. 12 Positional connections require more complex couplings with locknuts or special positional couplings. They require strict torque control, which is a key QA/QC parameter.

- CADWELD (Exothermic): Provides maximum strength, but is limited by process complexity, weather sensitivity, and the need for specialized personnel, reducing productivity compared to mechanical threaded or extruded systems.

6.3. Engineering Recommendations

In the context of strategic and engineering consulting support for projects (for example, in South-Eastern Europe, where the development of nuclear infrastructure is planned), the following principles should be followed when selecting reinforcement technologies:

- Strict Compliance with Bar Break Requirements: Mandatory requirement for Type 2 (Bar Break) mechanical couplings , which must be certified to international standards such as ASME NCA-3800 and ISO 19443:2018 , regardless of the reactor's country of origin. This ensures the required safety margin (1.25 times the actual yield strength) and ductility in critical areas.

- Prioritizing QA/QC over Cost: When choosing between systems of comparable strength (e.g., Griptec vs. Bartec/LENTON), preference should be given to systems that provide maximum traceability and automated quality control of each connection (e.g., Griptec with its 100% testing). 15 In regions with potentially limited availability of highly skilled labor, this approach becomes a strategic risk mitigation tool by minimizing dependence on human error.

- Using Mechanical Splices as a Project Management Tool: The use of mechanical splices is not just a technical solution, but a key factor in eliminating rebar clutter, which is critical to ensuring the quality of concreting for massive nuclear structures. 11 It also enables the efficient implementation of modular construction methods, accelerating the work schedule.

VII. CONCLUSION: STRATEGIC IMPLICATIONS

A global analysis of leading Gen III+ NPP projects (Russia, Korea, USA, China, France) demonstrates that the rebar in critical load-bearing structures, such as the containment and foundation slab, has large diameters (up to Ø57 mm / #18) and requires exceptional splice strength. Traditional lap splicing has been completely eliminated from critical areas because it does not provide the required ductility, creates reinforcement clutter, and compromises the quality of concreting.

Full-performance mechanical coupling technology (Type 2 / Bar Break) has been adopted as a universal solution. This technological homogenization is dictated not by economics, but by strict regulatory requirements, where ASME BPV Code Section III, Division 2 standards are the global benchmark.

The market for these critical components is controlled by two major global suppliers: Dextra Group (Griptec® and Bartec® systems) and nVent LENTON (LENTON® and CADWELD® systems). The fact that key projects such as the French EPR (Dextra Griptec®) and the Russian VVER-1200 in Turkey (Dextra Bartec®/Griptec®) utilize products from the same international manufacturer, certified to ASME NCA-3800 and ISO 19443, underscores that reliability, traceability, and compliance with global safety standards are a top priority, overriding national or vendor preferences.

Sources

- Tier 2 Chapter 03—Design of Structures, Systems, Components, and Nuclear Regulatory Commission, accessed October 2, 2025, https://www.nrc.gov/docs/ml1328/ml13281a729.pdf

- IAEA Nuclear Energy Series Construction Technologies for Nuclear Power Plants, accessed October 2, 2025, https://www-pub.iaea.org/MTCD/Publications/PDF/P1526_Web.pdf

- REBAR COUPLER SYSTEMS - The British Association of Reinforcement, accessed October 2, 2025, https://uk-bar.org/uploads/documents/originals/134230%20BAR%20Tech%20Rebar%20Couplers%20WEB%20(1).pdf

- Nuclear – Dextra Group | Reliable Connections, accessed October 2, 2025, https://www.dextragroup.com/applications/nuclear/

- "Design Review of Cadweld Reinforcing Bar Splice System," technical evaluation rept., accessed October 2, 2025, https://www.nrc.gov/docs/ML1719/ML17198A197.pdf

- Docket ID NRC-2020-0159 Topic: DG-1372, PROPOSED REVISION 4 TO REGULAT - Regulations.gov, last accessed: October 2, 2025, https://downloads.regulations.gov/NRC-2020-0159-0005/attachment_1.pdf

- Product Datasheet | Griptec - Fletcher Reinforcing, accessed October 2, 2025, https://www.fletcherreinforcing.co.nz/web/assets/J010721_FLET_FR_Dextra_Griptec_Datasheet_Brochure_UPDATE_May_2023-1.pdf

- Rebar Sizes, Grades, and Types - BigRentz, accessed October 2, 2025, https://www.bigrentz.com/blog/rebar-sizes

- Local Behavior of Lap-Spliced Deformed Rebars in Reinforced Concrete Beams - MDPI, accessed October 2, 2025, https://www.mdpi.com/1996-1944/14/23/7186

- Techniques Used for Bond Strengthening of Sub-Standard Splices in Concrete: A Review Study - MDPI, accessed October 2, 2025, https://www.mdpi.com/2227-9717/11/4/1119

- Nuclear and Rail | nVent LENTON, accessed October 2, 2025, https://nvent.com/en-gt/lenton/nuclear-and-rail-nvent-lenton

- Standard Couplers | nVent LENTON, accessed October 2, 2025, https://www.nvent.com/en-us/lenton/products/standard-couplers

- nVent LENTON - Concrete Reinforcing Couplers & Anchors, accessed October 2, 2025, https://www.nvent.com/en-us/lenton

- Rebar Couplers – Dextra Group | Reliable Connections, accessed October 2, 2025, https://www.dextragroup.com/concrete-reinforcement-solutions-old/rebar-couplers/

- Flamanville EPR | Dextra Group | Reliable Connections, accessed October 2, 2025, https://www.dextragroup.com/flamanville-epr/

- Bartec: Setting the Global Standard for Rebar Splicing - Dextra Group, accessed October 2, 2025, https://www.dextragroup.com/concrete-reinforcement-solutions/rebar-couplers/bartec/

- Bartek BP Rebar Splice System - SRG Global | Engineered Products, accessed October 2, 2025, https://srgglobalproducts.com.au/engineered-products/rebar-couplers/bartek-bp-rebar-splice-system/

- Full-System Solutions | nVent LENTON, accessed October 2, 2025, https://www.nvent.com/en-us/lenton/solutions/full-system-planning

- Lenton Threading Couplers - Pacific Bolt Manufacturing, accessed October 2, 2025, https://pacbolt.com/lenton-threading-couplers/

- EPR (nuclear reactor) - Wikipedia, accessed October 2, 2025, https://en.wikipedia.org/wiki/EPR_(nuclear_reactor)

- Hinkley Point C nuclear power station - Wikipedia, accessed October 2, 2025, https://en.wikipedia.org/wiki/Hinkley_Point_C_nuclear_power_station

- Hinkley Point C Nuclear Power Plant – Dextra Group | Reliable Connections, accessed October 2, 2025, https://www.dextragroup.com/hinkley-point-c-nuclear-power-plant/

- AP1000 - Wikipedia, last accessed October 2, 2025, https://en.wikipedia.org/wiki/AP1000

- Westinghouse Celebrates Milestone Achievement as AP1000® Technology Powers Plant Vogtle Unit 4 into Commercial Operation, accessed October 2, 2025, https://info.westinghousenuclear.com/news/westinghouse-celebrates-milestone-achievement-as-ap1000-technology-powers-plant-vogtle-unit-4-into-commercial-operation

- AP1000® Pressurized Water Reactor - Westinghouse Nuclear, accessed October 2, 2025, https://westinghousenuclear.com/energy-systems/ap1000-pwr/

- APR-1400 - Wikipedia, accessed October 2, 2025, https://en.wikipedia.org/wiki/APR-1400

- Technology - ENEC, last accessed: October 2, 2025, https://www.enec.gov.ae/barakah-plant/technology/

- Frequently Asked Questions About the Barakah Plant - ENEC, accessed October 2, 2025, https://www.enec.gov.ae/barakah-plant/frequently-asked-questions/

- Rosatom started the final assembly of the reactor for Akkuyu NPP Unit 4, last accessed: October 2, 2025, https://akkuyu.com/en/news/rosatom-started-the-final-assembly-of-the-reactor-for-akkuyu-npp-unit-4

- Facts | AKKUYU NÜKLEER A.Ş., last accessed: October 2, 2025, https://akkuyu.com/en/facts

- Akkuyu Nuclear Power Plant – Dextra Group | Reliable Connections, accessed October 2, 2025, https://www.dextragroup.com/akkuyu-nuclear-power-plant/

- World's first Hualong One reactor put into commercial operation, accessed October 2, 2025, https://en.cnnc.com.cn/2021-01/30/c_1023234.htm

- Commissioning Fuqing 5&6 - World Nuclear Association, accessed October 2, 2025, https://world-nuclear.org/our-association/publications/world-nuclear-performance-report/commissioning-fuqing-56

- Rebar couplers – Dextra Group | Reliable Connections, accessed October 2, 2025, https://www.dextragroup.com/concrete-reinforcement-solutions/rebar-couplers/

- Dextra Griptec® Standard Couplers – Mechanical Splices - InfraBuild, accessed October 2, 2025, https://www.infrabuild.com/reinforcing/products/accessories/dextra-griptec-standard-couplers-mechanical-splice/